## INPUT DATA
Input values
CHP: power to heat ratio = | 2.5 |  | 1)
Heat pump: heat/power = | 3.5
Boiler efficiency of the CHP plant = | 90% |  | 2)
CHP electricity used for internal process in CHP = | 6% | of CHP electricity generation | 3)
Separate electricity generation: efficiency = | 33%
Clarifications:
1) 2,5 for solid fuel power plants and gas turbines but about 1,0 for combined cycle power plants and diesel/gas engines
2) 85-91% for solid fuel plants but 93-98% for natural gas plants
3) 6-10% for solid fuel plants but about 1-2% for gas fuelled plants

## OUTPUT
Electricity |  |  |  | Heat |  |  | Primary | CHP | Prim.
Total | CHP | Separate | Heat pump | Total | CHP | Heat pump | energy | heat | energia
40 | 40 | 0 | 0 | 100 | 100 | 0 | 158.2222 | 0 | 207.7922
42.8571 | 36 | 4 | 2.8571 | 100 | 90 | 10 | 163.1792 | 10 | 202.8352
45.7143 | 32 | 8 | 5.7143 | 100 | 80 | 20 | 168.1362 | 20 | 197.8782
48.5714 | 28 | 12 | 8.5714 | 100 | 70 | 30 | 173.0932 | 30 | 192.9212
51.4286 | 24 | 16 | 11.4286 | 100 | 60 | 40 | 178.0502 | 40 | 187.9642
54.2857 | 20 | 20 | 14.2857 | 100 | 50 | 50 | 183.0072 | 50 | 183.0072
57.1429 | 16 | 24 | 17.1429 | 100 | 40 | 60 | 187.9642 | 60 | 178.0502
60 | 12 | 28 | 20 | 100 | 30 | 70 | 192.9212 | 70 | 173.0932
62.8571 | 8 | 32 | 22.8571 | 100 | 20 | 80 | 197.8782 | 80 | 168.1362
65.7143 | 4 | 36 | 25.7143 | 100 | 10 | 90 | 202.8352 | 90 | 163.1792
68.5714 | 0 | 40 | 28.5714 | 100 | 0 | 100 | 207.7922 | 100 | 158.2222